## Totals
HISTORY
3/02/2025 - V1 | Initial version of the protocol
4/02/2025 - V2 | Fix address overlap
3/04/2025 - V3 | Fix signed vs unsigned
5/04/2025 - V4 | Added some comments
SCOPE
This protocol is intended to be used by single inverters, PLC's, gateways and external controllers that want to integrate with the Eniris SmartgridOne EMS.
In this setup, the Eniris SmartgridOne EMS is the master, and the inverter / PLC / gateway / external controller the slave.
Both Modbus RTU and Modbus TCP are supported.
NOTE for PLC's, gateways and external controllers
If you have multiple inverters connected to the PLC, gateway or external controller, then through this protocol they will be present as a single big inverter to the Eniris SmartgridOne EMS.
The consequence is that it will not be generally possible for the Eniris SmartgridOne EMS to safeguard internal AC current flows if your inverters in the electrical installation are not also physically grouped together.
REMARKS
- For Modbus TCP, you must respond on Modbus ID 1.
- Register addresses start counting at 0
- All the registers are big endian
- If a register is not implemented, then it must contain the following value:
| 16 bit unsigned integer | 0xFFFF
| 32 bit unsigned integer | 0xFFFFFFFF
| 64 bit unsigned integer | 0xFFFFFFFFFFFFFFFF
| 16 bit signed integer | 0x8000
| 32 bit signed integer | 0x80000000
| 64 bit signed integer | 0x8000000000000000
- Write registers that are not implemented should still be writeable
- Recommended registers are not strictly necessary for normal use cases, but they improve the accuracy of the EMS and may be required for guarding against overloads.
READ ONLY REGISTERS
To be supported Modbus Functions: Read Input Registers (0x04)
Address | Type | Size | Unit | Variable | Mandatory | Comments
M: Mandatory
R: Recommended
O: Optional
General fields
0 | 32 bit unsigned integer | 2 | - | Fixed number for identification purposes | M | This register MUST always hold the value "0x454E4952" (it is used to identify that this device follows this protocol)
2 | String (UTF-8) | 16 | - | Manufacturer | R | Pad with spaces (0x20) or end string with 0x0
18 | String (UTF-8) | 16 | - | Serial number | R
34-99 | Reserved
Grid energy meter
Always required fields:
100 | 16 bit unsigned integer | 1 | - | Grid energy meter presence | M | 0 = No grid energy meter 1 = There is a grid energy meter.
The following fields may be set to the unimplemented value if there is no grid energy meter:
101 | 32 bit signed integer | 2 | W | Total active power | M | Negative is towards the grid, positive is towards the installation
103 | 16 bit unsigned integer | 1 | A | Current L1 | R
104 | 16 bit unsigned integer | 1 | A | Current L2 | R
105 | 16 bit unsigned integer | 1 | A | Current L3 | R
106 | 16 bit unsigned integer | 1 | A | Current N | O
107 | 16 bit unsigned integer | 1 | V | Voltage L1-N | R
108 | 16 bit unsigned integer | 1 | V | Voltage L2-N | R
109 | 16 bit unsigned integer | 1 | V | Voltage L3-N | R
110 | 16 bit unsigned integer | 1 | V | Voltage L1-L2 | R
111 | 16 bit unsigned integer | 1 | V | Voltage L2-L3 | R
112 | 16 bit unsigned integer | 1 | V | Voltage L3-L1 | R
113 | 16 bit unsigned integer | 1 | mHz (0.001 Hz) | Frequency | R
114 | 32 bit signed integer | 2 | W | Active power L1 | R | Negative is towards the grid, positive is towards the installation
116 | 32 bit signed integer | 2 | W | Active power L2 | R | Negative is towards the grid, positive is towards the installation
118 | 32 bit signed integer | 2 | W | Active power L3 | R | Negative is towards the grid, positive is towards the installation
120 | 32 bit signed integer | 2 | VAr | Total reactive power | R | Negative is capacitive behaviour of the installation, positive is inductive behaviour of the installation
122 | 32 bit signed integer | 2 | VAr | Reactive power L1 | O | Negative is capacitive behaviour of the installation, positive is inductive behaviour of the installation
124 | 32 bit signed integer | 2 | VAr | Reactive power L2 | O | Negative is capacitive behaviour of the installation, positive is inductive behaviour of the installation
126 | 32 bit signed integer | 2 | VAr | Reactive power L3 | O | Negative is capacitive behaviour of the installation, positive is inductive behaviour of the installation
128 | 64 bit unsigned integer | 4 | 0.1 kWh | Total import active energy | R
132 | 64 bit unsigned integer | 4 | 0.1 kWh | Total export active energy | R
136 | 64 bit unsigned integer | 4 | 0.1 kVArh | Total inductive reactive energy | R
140 | 64 bit unsigned integer | 4 | 0.1 kVArh | Total capacitive reactive energy | R
144-199 | Reserved
Totals of the AC side of all PV inverters, storage inverters and hybrid inverters
The following fields may be set to the unimplemented value if and only if there is no PV AND there is no battery storage
200 | 32 bit signed integer | 2 | W | Nominal power | R | Total nominal power
202 | 32 bit signed integer | 2 | W | Total active power | M | Negative is towards the grid, positive is towards the installation
204 | 16 bit unsigned integer | 1 | A | Current L1 | R
205 | 16 bit unsigned integer | 1 | A | Current L2 | R
206 | 16 bit unsigned integer | 1 | A | Current L3 | R
207 | 16 bit unsigned integer | 1 | A | Current N | O
208 | 32 bit signed integer | 2 | W | Active power L1 | R | Negative is towards the grid, positive is towards the installation
210 | 32 bit signed integer | 2 | W | Active power L2 | R | Negative is towards the grid, positive is towards the installation
212 | 32 bit signed integer | 2 | W | Active power L3 | R | Negative is towards the grid, positive is towards the installation
214 | 32 bit signed integer | 2 | VAr | Total reactive power | R | Negative is capacitive behaviour of the installation, positive is inductive behaviour of the installation
216 | 32 bit signed integer | 2 | VAr | Reactive power L1 | O | Negative is capacitive behaviour of the installation, positive is inductive behaviour of the installation
218 | 32 bit signed integer | 2 | VAr | Reactive power L2 | O | Negative is capacitive behaviour of the installation, positive is inductive behaviour of the installation
220 | 32 bit signed integer | 2 | VAr | Reactive power L3 | O | Negative is capacitive behaviour of the installation, positive is inductive behaviour of the installation
222 | 64 bit unsigned integer | 4 | 0.1 kVArh | Total inductive reactive energy | R
226 | 64 bit unsigned integer | 4 | 0.1 kVArh | Total capacitive reactive energy | R
230-299 | Reserved
Total PV data fields
Always required fields:
300 | 16 bit unsigned integer | 1 | - | PV presence | M | 0 = No PV. 1 = There is PV.
The following fields may be set to the unimplemented value if there is no PV:
301 | 32 bit signed integer | 2 | W | Nominal power | R | Total nominal PV power
303 | 32 bit unsigned integer | 2 | W | Total active power | M | Always positive for production
305 | 64 bit unsigned integer | 4 | 0.1 kWh | Total produced energy | R
309 | 16 bit unsigned integer | 1 | - | PV Control followed / not followed | R | 0 = Control of PV by the EMS is permitted and active; 1 = Control signals for the PV by the EMS will be ignored
310-399 | Reserved
Total battery storage data fields
Always required fields:
400 | 16 bit unsigned integer | 1 | - | Battery storage presence | M | 0 = No battery storage 1 = There is battery storage.
The following fields may be set to the unimplemented value if there is no battery storage:
401 | 32 bit signed integer | 2 | W | Nominal power | R | Total nominal battery storage power
403 | 32 bit unsigned integer | 2 | 0.1 kWh | Total battery capacity | R | Total battery storage capacity
405 | 32 bit signed integer | 2 | W | Total active power | M | Negative is discharging, positive is charging
407 | 16 bit unsigned integer | 1 | 0.1% | State of charge | M | Must be between 0% and 100%
408 | 64 bit unsigned integer | 4 | 0.1 kWh | Total charged energy | R
412 | 64 bit unsigned integer | 4 | 0.1 kWh | Total discharged energy | R
416 | 16 bit unsigned integer | 1 | - | Battery storage control followed / not followed | R | 0 = Control of battery storage by the EMS is permitted and active; 1 = Control signals for the battery storage by the EMS will be ignored
417-499 | Reserved
READ/WRITE REGISTERS
To be supported Modbus functions: Read Holding Registers (0x03), Write Single Holding Register (0x06), Write Multiple Holding Registers (0x10)
Address | Type | Size | Unit | Variable | Mandatory | Comments
M: Mandatory
R: Recommended
O: Optional
1000 | 16 bit unsigned integer | 1 | seconds | Watchdog fallback time | R | If the Eniris SmartgridOne EMS does not send a control value within this time, then fall back to a safe state. You are free to choose what this safe state is, but a good recommendation is maximum production for PV and self consumption for storage. The Eniris SmartgridOne EMS will set this fallback time! If your device implements a fallback mechanism, then this register is MANDATORY.
1001 | 16 bit unsigned integer | 1 | - | Remote control active | M | 0 = Remote control is not active. Your device controls itself. 1 = Remote control is active. Your device is controlled by the Eniris SmartgridOne EMS. | TODO WE NEED THIS FOR PV, BATTERY SEPARATE
1002 | 32 bit unsigned integer | 2 | W | Total PV power setpoint | M | PV power setpoint. This is the maximum power that the PV may produce.
1004 | 32 bit signed integer | 2 | W | Total battery power setpoint | M | Battery storage power setpoint. Negative is discharging, positive is charging.
1006 | 32 bit signed integer | 2 | VAr | Total inverter AC reactive power setpoint | O | Reactive power setpoint. Negative is capacitive, positive is inductive
1008-1099 | Reserved